WMF21 Series

NTC Thermistors负温度系数热敏电阻器

- For Limiting of Inrush Current用于抑制浪涌电流

■ GENERAL 概述

WEILIN WMF21 series NTC thermistors are used for limiting the Inrush Current in the power supply loop of every kinds of power supply, ballast / CFL etc. and the heating loop of CRT of color TV / monitor, heater, filament etc. The WMF21 series complies with the UL1434，and owns the passport of UL.

The WMF21 series NTC thermistors is the radial leads resin coating type products, it has the characteristic of small bulk, high power, strong limiting of inrush current, quick response, long life, high reliability, etc. The temperature is decreased while the Material Consistent(B) of NTC thermisters is increasing and the Remain Resistance is decreasing. The higher is the Thermal Capacity, the stronger is the capability of limiting the Inrush Current. It is direct proportion to the product of the Thermal Time Constant (τ) and Thermal Dissipation Constant () .

The WMF21 series NTC thermistors has so wide application area, which is mainly used in Switching Power Supply, UPS Power Supply, CFL, Ballast, Circuitry of Power Supply, etc.

偉林WMF21系列NTC热敏电阻器主要用于抑制各类电源、电子镇流器/节能灯等电源回路和彩色显像管、加热器、灯丝等电路开机瞬间产生的浪涌电流。WMF21系列产品符合美国UL1434标准要求，已通过美国UL安全认证。

WMF21系列产品为引线焊接树脂涂装型，体积小功率大、抑制浪涌电流强、反应速度快、产品使用寿命长、可靠性高等特点。 NTC热敏电阻材料常数（即B值）β越大，残余电阻RR越小，则温升越低。NTC热敏电阻热容量愈大，抑制浪涌电流的能力愈强。热容量与热时间常数τ和热耗散系数δ之乘积成正比。

WMF21产品主要应用在开关电源、UPS电源、电子节能灯、电子镇流器、电源线路等，应用范围广泛。

■ PART NUMBERING 产品编号

| WMF21 | - | 5 | - | D9 | M | S | U | P | 5 | C | B |  | 5 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

⑴       ⑵      ⑶   ⑷   ⑸    ⑹   ⑺   ⑻   ⑼   ⑽      ⑾

⑴ Series系列: WMF21 - For limiting of inrush current

⑵ Rated Zero Power Resistance额定零功率电阻:  5 - 5Ω    10 - 10Ω

⑶ Disc. Diameter芯片尺寸:  D9 - 9mm   D15 - 15mm

⑷ Tolerance of Resistance阻值允差:  M - ±20%   K - ±10%

⑸ Coating Material包封材料：S- Silicone 硅树脂		N - No Coating无包封

P - PF Resin 酚酫树脂   	E - Epoxy 环氧树脂

⑹Shape of Leads引线形状：U - In-formed内弯   	S - Straight直形

A - Axis Formed轴弯	O- Out-Formed外弯

N - No Leads 无引线

⑺Leads material引线材质：P：Cp 钢线  U：Cu 铜线

⑻ Leads diameter引线直径 5-Φ0.5  6-Φ0.6  8-Φ0.8

⑼ Leads space引线间距 A-3，B-5，C-7.5，D-10

⑽ Packing Type包装形式：B - Bulk 散装  A - Ammo 条带  R - Reel 盘带

⑾ Leads length引脚长度：5-5.0 mm，20-20mm

■ SPECIFICATION S TABLE规格表

| No. 序号 |  | Part No. 产品编号 | Rated Zero-power Resistance 额定 零功率电阻 RN (Ω) | Max. Steady State Current 最大 稳态电流 Imax (A) | Remain. Resistance 残余电阻 RR (Ω) | Max.Load Capacitancein in uF 最大允许 容量 @ 240VAC (uF) | Thermal Dissipation Constant 热耗散 系数 δ(mW/℃) | Thermal Time Constant 热时间 常数 τ(Sec) | Max.power Rating 最大额定 功率 @ 25℃ Pmax(W) | Operating Temperature工作温度 (℃) | Dimensions 外形尺寸 (mm) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  | DMax | TMax | d±0.05 | F±1 |
| 01 | WMF21-1.5D-5M |  | 1.5±20% | 1 | 0.087 | 68 | Approx. 15 | Approx. 17 | 1.5 | -40~+150 | 6.5 | 5 | 0.6 (0.45) | 5 |
| 02 | WMF21-2D-5M |  | 2.0±20% | 1 | 0.095 | 68 |  |  |  |  |  |  |  |  |
| 03 | WMF21-2.5D-5M |  | 2.5±20% | 1 | 0.123 | 68 |  |  |  |  |  |  |  |  |
| 04 | WMF21-3D-5M |  | 3±20% | 1 | 0.198 | 68 |  |  |  |  |  |  |  |  |
| 05 | WMF21-5D-5M |  | 5±20% | 1 | 0.353 | 68 |  |  |  |  |  |  |  |  |
| 06 | WMF21-7D-5M |  | 7±20% | 0.8 | 0.426 | 68 |  |  |  |  |  |  |  |  |
| 07 | WMF21-8D-5M |  | 8±20% | 0.8 | 0.524 | 68 |  |  |  |  |  |  |  |  |
| 08 | WMF21-10D-5M |  | 10±20% | 0.7 | 0.771 | 68 |  |  |  |  |  |  |  |  |
| 09 | WMF21-12D-5M |  | 12±20% | 0.7 | 0.867 | 68 |  |  |  |  |  |  |  |  |
| 10 | WMF21-15D-5M |  | 15±20% | 0.6 | 0.90 | 68 |  |  |  |  |  |  |  |  |
| 11 | WMF21-16D-5M |  | 16±20% | 0.6 | 0.925 | 68 |  |  |  |  |  |  |  |  |
| 12 | WMF21-20D-5M |  | 20±20% | 0.6 | 0.996 | 68 |  |  |  |  |  |  |  |  |
| 13 | WMF21-22D-5M |  | 22±20% | 0.6 | 1.028 | 68 |  |  |  |  |  |  |  |  |
| 14 | WMF21-30D-5M |  | 30±20% | 0.5 | 1.134 | 68 |  |  |  |  |  |  |  |  |
| 15 | WMF21-33D-5M |  | 33±20% | 0.5 | 1.20 | 68 |  |  |  |  |  |  |  |  |
| 16 | WMF21-36D-5M |  | 36±20% | 0.5 | 1.323 | 68 |  |  |  |  |  |  |  |  |
| 17 | WMF21-47D-5M |  | 47±20% | 0.4 | 1.50 | 68 |  |  |  |  |  |  |  |  |
| 18 | WMF21-50D-5M |  | 50±20% | 0.4 | 1.632 | 68 |  |  |  |  |  |  |  |  |
| 19 | WMF21-60D-5M |  | 60±20% | 0.4 | 1.878 | 47 |  |  |  |  |  |  |  |  |
| 20 | WMF21-68D-5M |  | 68±20% | 0.4 | 2.10 | 47 |  |  |  |  |  |  |  |  |
| 21 | WMF21-200D-5M |  | 200±20% | 0.1 | 18.7 | 47 |  |  |  |  |  |  |  |  |
| 22 | WMF21-1.5D-7M |  | 1.5±20% | 2 | 0.213 | 100 | Approx. 16 | Approx. 27 | 1.8 | -40~+150 | 8.5 | 5 | 0.6 | 5 |
| 23 | WMF21-2D-7M |  | 2±20% | 2 | 0.243 | 100 |  |  |  |  |  |  |  |  |
| 24 | WMF21-3D-7M |  | 3±20% | 2 | 0.266 | 100 |  |  |  |  |  |  |  |  |
| 25 | WMF21-5D-7M |  | 5±20% | 2 | 0.283 | 100 |  |  |  |  |  |  |  |  |
| 26 | WMF21-7D-7M |  | 7±20% | 1 | 0.432 | 100 |  |  |  |  |  |  |  |  |
| 27 | WMF21-8D-7M |  | 8±20% | 1 | 0.539 | 100 |  |  |  |  |  |  |  |  |
| 28 | WMF21-10D-7M |  | 10±20% | 1 | 0.616 | 100 |  |  |  |  |  |  |  |  |
| 29 | WMF21-12D-7M |  | 12±20% | 1 | 0.816 | 100 |  |  |  |  |  |  |  |  |
| 30 | WMF21-15D-7M |  | 15±20% | 0.7 | 0.997 | 100 |  |  |  |  |  |  |  |  |
| 31 | WMF21-16D-7M |  | 16±20% | 0.7 | 1.003 | 100 |  |  |  |  |  |  |  |  |
| 32 | WMF21-20D-7M |  | 20±20% | 0.7 | 1.096 | 100 |  |  |  |  |  |  |  |  |
| 33 | WMF21-22D-7M |  | 22±20% | 0.6 | 1.108 | 100 |  |  |  |  |  |  |  |  |
| 34 | WMF21-33D-7M |  | 33±20% | 0.5 | 1.485 | 100 |  |  |  |  |  |  |  |  |
| 35 | WMF21-50D-7M |  | 50±20% | 0.3 | 2.657 | 100 |  |  |  |  |  |  |  |  |
| 36 | WMF21-200D-7MM |  | 200±20% | 0.2 | 11.65 | 68 |  |  |  |  |  |  |  |  |
| 37 | WMF21-1.5D-9M |  | 1.5±20% | 4 | 0.093 | 200 | Approx. 16 | Approx. 38 | 2.0 | -40~+170 | 10.5 | 5.5 | 0.8 (0.6) | 7.5 (5) |
| 38 | WMF21-2.5D-9M |  | 2.5±20% | 4 | 0.108 | 200 |  |  |  |  |  |  |  |  |
| 39 | WMF21-3D-9M |  | 3±20% | 4 | 0.120 | 200 |  |  |  |  |  |  |  |  |
| 40 | WMF21-4D-9M |  | 4±20% | 3 | 0.190 | 200 |  |  |  |  |  |  |  |  |
| 41 | WMF21-4.7D-9M |  | 4.7±20% | 3 | 0.202 | 200 |  |  |  |  |  |  |  |  |
| 42 | WMF21-5D-9M |  | 5±20% | 3 | 0.210 | 200 |  |  |  |  |  |  |  |  |
| 43 | WMF21-6D-9M |  | 6±20% | 2 | 0.315 | 200 |  |  |  |  |  |  |  |  |
| 44 | WMF21-8D-9M |  | 8±20% | 2 | 0.400 | 200 |  |  |  |  |  |  |  |  |
| 45 | WMF21-10D-9M |  | 10±20% | 2 | 0.458 | 200 |  |  |  |  |  |  |  |  |
| 46 | WMF21-12D-9M |  | 12±20% | 1 | 0.652 | 200 |  |  |  |  |  |  |  |  |
| 47 | WMF21-15D-9M |  | 15±20% | 1 | 0.793 | 200 |  |  |  |  |  |  |  |  |
| 48 | WMF21-16D-9M |  | 16±20% | 1 | 0.802 | 200 |  |  |  |  |  |  |  |  |
| 49 | WMF21-20D-9M |  | 20±20% | 1 | 0.864 | 200 |  |  |  |  |  |  |  |  |
| 50 | WMF21-22D-9M |  | 22±20% | 1 | 0.950 | 200 |  |  |  |  |  |  |  |  |
| 51 | WMF21-30D-9M |  | 30±20% | 1 | 1.022 | 200 |  |  |  |  |  |  |  |  |
| 52 | WMF21-33D-9M |  | 33±20% | 1 | 1.124 | 200 |  |  |  |  |  |  |  |  |
| 53 | WMF21-50D-9M |  | 50±20% | 1 | 1.252 | 200 |  |  |  |  |  |  |  |  |
| 54 | WMF21-60D-9M |  | 60±20% | 0.8 | 1.502 | 200 |  |  |  |  |  |  |  |  |
| 55 | WMF21-80D-9M |  | 80±20% | 0.8 | 2.010 | 150 |  |  |  |  |  |  |  |  |
| 56 | WMF21-120D-9M |  | 120±20% | 0.8 | 3.015 | 150 |  |  |  |  |  |  |  |  |
| 57 | WMF21-200D-9M |  | 200±20% | 0.5 | 5.007 | 150 |  |  |  |  |  |  |  |  |
| 58 | WMF21-400D-9M |  | 400±20% | 0.2 | 9.852 | 150 |  |  |  |  |  |  |  |  |

| No. 序号 | Part No. 产品编号 | Rated Zero-power Resistance 额定 零功率电阻 RN (Ω) | Max. Steady State Current 最大 稳态电流 Imax (A) | Remain. Resistance 残余电阻 RR (Ω) | Max.Load Capacitancein in uF 最大允许 容量 @ 240VAC (uF) | Thermal Dissipation Constant 热耗散 系数 δ(mW/℃) | Thermal Time Constant 热时间 常数 τ(Sec) | Max.power Rating 最大额定 功率 @ 25℃ Pmax(W) | Operating Temperature工作温度 (℃) | Dimensions 外形尺寸 (mm) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | DMax | TMax | d±0.05 | F±1 |
| 59 | WMF21-1D-10M | 1±20% | 5 | 0.091 | 300 | Approx. 17 | Approx. 43 | 2.3 | -40~+170 | 11.5 | 5.5 | 0.8 (0.6) | 7.5 (5) |
| 60 | WMF21-1.3D-10M | 1.3±20% | 5 | 0.095 | 300 |  |  |  |  |  |  |  |  |
| 61 | WMF21-1.5D-10M | 1.5±20% | 5 | 0.101 | 300 |  |  |  |  |  |  |  |  |
| 62 | WMF21-2D-10M | 2±20% | 5 | 0.112 | 300 |  |  |  |  |  |  |  |  |
| 63 | WMF21-2.5D-10M | 2.5±20% | 5 | 0.120 | 300 |  |  |  |  |  |  |  |  |
| 64 | WMF21-3D-10M | 3±20% | 5 | 0.127 | 300 |  |  |  |  |  |  |  |  |
| 65 | WMF21-3.3D-10M | 3.3±20% | 5 | 0.135 | 300 |  |  |  |  |  |  |  |  |
| 66 | WMF21-4D-10M | 4±20% | 4 | 0.167 | 300 |  |  |  |  |  |  |  |  |
| 67 | WMF21-5D-10M | 5±20% | 4 | 0.180 | 300 |  |  |  |  |  |  |  |  |
| 68 | WMF21-6D-10M | 6±20% | 3 | 0.343 | 300 |  |  |  |  |  |  |  |  |
| 69 | WMF21-6.8D-10M | 6.8±20% | 3 | 0.370 | 300 |  |  |  |  |  |  |  |  |
| 70 | WMF21-8D-10M | 8±20% | 3 | 0.405 | 300 |  |  |  |  |  |  |  |  |
| 71 | WMF21-10D-10M | 10±20% | 3 | 0.497 | 300 |  |  |  |  |  |  |  |  |
| 72 | WMF21-12D-10M | 12±20% | 2 | 0.667 | 300 |  |  |  |  |  |  |  |  |
| 73 | WMF21-15D-10M | 15±20% | 2 | 0.692 | 300 |  |  |  |  |  |  |  |  |
| 74 | WMF21-16D-10M | 16±20% | 2 | 0.702 | 300 |  |  |  |  |  |  |  |  |
| 75 | WMF21-20D-10M | 20±20% | 2 | 0.746 | 300 |  |  |  |  |  |  |  |  |
| 76 | WMF21-22D-10M | 22±20% | 2 | 0.759 | 300 |  |  |  |  |  |  |  |  |
| 77 | WMF21-25D-10M | 25±20% | 1.5 | 0.978 | 300 |  |  |  |  |  |  |  |  |
| 78 | WMF21-30D-10M | 30±20% | 1.5 | 1.003 | 300 |  |  |  |  |  |  |  |  |
| 79 | WMF21-33D-10M | 33±20% | 1.5 | 1.032 | 220 |  |  |  |  |  |  |  |  |
| 80 | WMF21-47D-10M | 47±20% | 1.5 | 1.078 | 220 |  |  |  |  |  |  |  |  |
| 81 | WMF21-50D-10M | 50±20% | 1.5 | 1.116 | 220 |  |  |  |  |  |  |  |  |
| 82 | WMF21-60D-10M | 60±20% | 1 | 1.864 | 220 |  |  |  |  |  |  |  |  |
| 83 | WMF21-80D-10M | 80±20% | 1 | 2.236 | 220 |  |  |  |  |  |  |  |  |
| 84 | WMF21-1D-11M | 1±20% | 5 | 0.072 | 300 | Approx. 17 | Approx. 45 | 2.4 | -40~+170 | 12.5 | 5.5 | 0.8 (0.6) | 7.5 (5) |
| 85 | WMF21-1.3D-11M | 1.3±20% | 5 | 0.077 | 300 |  |  |  |  |  |  |  |  |
| 86 | WMF21-1.5D-11M | 1.5±20% | 5 | 0.083 | 300 |  |  |  |  |  |  |  |  |
| 87 | WMF21-2D-11M | 2±20% | 5 | 0.092 | 300 |  |  |  |  |  |  |  |  |
| 88 | WMF21-2.5D-11M | 2.5±20% | 5 | 0.095 | 300 |  |  |  |  |  |  |  |  |
| 89 | WMF21-3D-11M | 3±20% | 5 | 0.100 | 300 |  |  |  |  |  |  |  |  |
| 90 | WMF21-3.3D-11M | 3.3±20% | 5 | 0.127 | 300 |  |  |  |  |  |  |  |  |
| 91 | WMF21-4D-11M | 4±20% | 4 | 0.150 | 300 |  |  |  |  |  |  |  |  |
| 92 | WMF21-5D-11M | 5±20% | 4 | 0.156 | 300 |  |  |  |  |  |  |  |  |
| 93 | WMF21-6D-11M | 6±20% | 3 | 0.240 | 300 |  |  |  |  |  |  |  |  |
| 94 | WMF21-6.8D-11M | 6.8±20% | 3 | 0.247 | 300 |  |  |  |  |  |  |  |  |
| 95 | WMF21-8D-11M | 8±20% | 3 | 0.255 | 300 |  |  |  |  |  |  |  |  |
| 96 | WMF21-10D-11M | 10±20% | 3 | 0.275 | 300 |  |  |  |  |  |  |  |  |
| 97 | WMF21-12D-11M | 12±20% | 2 | 0.462 | 300 |  |  |  |  |  |  |  |  |
| 98 | WMF21-15D-11M | 15±20% | 2 | 0.466 | 300 |  |  |  |  |  |  |  |  |
| 99 | WMF21-16D-11M | 16±20% | 2 | 0.470 | 300 |  |  |  |  |  |  |  |  |
| 100 | WMF21-20D-11M | 20±20% | 2 | 0.512 | 300 |  |  |  |  |  |  |  |  |
| 101 | WMF21-22D-11M | 22±20% | 2 | 0.563 | 300 |  |  |  |  |  |  |  |  |
| 102 | WMF21-25D-11M | 25±20% | 1.5 | 0.608 | 300 |  |  |  |  |  |  |  |  |
| 103 | WMF21-30D-11M | 30±20% | 1.5 | 0.667 | 300 |  |  |  |  |  |  |  |  |
| 104 | WMF21-33D-11M | 33±20% | 1.5 | 0.734 | 220 |  |  |  |  |  |  |  |  |
| 105 | WMF21-47D-11M | 47±20% | 1.5 | 0.926 | 220 |  |  |  |  |  |  |  |  |
| 106 | WMF21-50D-11M | 50±20% | 1.5 | 1.021 | 220 |  |  |  |  |  |  |  |  |
| 107 | WMF21-60D-11M | 60±20% | 1 | 1.215 | 220 |  |  |  |  |  |  |  |  |
| 108 | WMF21-80D-11M | 80±20% | 1 | 1.656 | 220 |  |  |  |  |  |  |  |  |
| 109 | WMF21-0.7D-13M | 0.7±20% | 7 | 0.049 | 560 | Approx. 18 | Approx. 66 | 3.1 | -40~+200 | 14.5 | 6 | 0.8/1.0 | 7.5 |
| 110 | WMF21-1D-13M | 1±20% | 7 | 0.056 | 560 |  |  |  |  |  |  |  |  |
| 111 | WMF21-1.3D-13M | 1.3±20% | 7 | 0.062 | 560 |  |  |  |  |  |  |  |  |
| 112 | WMF21-1.5D-13M | 1.5±20% | 7 | 0.073 | 560 |  |  |  |  |  |  |  |  |
| 113 | WMF21-2D-13M | 2±20% | 6 | 0.085 | 560 |  |  |  |  |  |  |  |  |
| 114 | WMF21-2.5D-13M | 2.5±20% | 6 | 0.088 | 560 |  |  |  |  |  |  |  |  |
| 115 | WMF21-3D-13M | 3±20% | 6 | 0.092 | 560 |  |  |  |  |  |  |  |  |
| 116 | WMF21-4D-13M | 4±20% | 5 | 0.120 | 560 |  |  |  |  |  |  |  |  |
| 117 | WMF21-4.7D-13M | 4.7±20% | 5 | 0.124 | 560 |  |  |  |  |  |  |  |  |
| 118 | WMF21-5D-13M | 5±20% | 5 | 0.125 | 560 |  |  |  |  |  |  |  |  |

| No. 序号 | Part No. 产品编号 | Rated Zero-power Resistance 额定 零功率电阻 RN (Ω) | Max. Steady State Current 最大 稳态电流 Imax (A) | Remain. Resistance 残余电阻 RR (Ω) | Max.Load Capacitancein in uF 最大允许 容量 @ 240VAC (uF) | Thermal Dissipation Constant 热耗散 系数 δ(mW/℃) | Thermal Time Constant 热时间 常数 τ(Sec) | Max.power Rating 最大额定 功率 @ 25℃ Pmax(W) | Operating Temperature工作温度 (℃) | Dimensions 外形尺寸 (mm) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | DMax | TMax | d±0.05 | F±1 |
| 119 | WMF21-6D-13M | 6±20% | 4 | 0.170 | 560 | Approx. 18 | Approx. 66 | 3.1 | -40~+200 | 14.5 | 6 | 0.8/1.0 | 7.5 |
| 120 | WMF21-7D-13M | 7±20% | 4 | 0.188 | 560 |  |  |  |  |  |  |  |  |
| 121 | WMF21-8D-13M | 8±20% | 4 | 0.194 | 560 |  |  |  |  |  |  |  |  |
| 122 | WMF21-10D-13M | 10±20% | 4 | 0.206 | 560 |  |  |  |  |  |  |  |  |
| 123 | WMF21-12D-13M | 12±20% | 3 | 0.316 | 560 |  |  |  |  |  |  |  |  |
| 124 | WMF21-15D-13M | 15±20% | 3 | 0.335 | 560 |  |  |  |  |  |  |  |  |
| 125 | WMF21-16D-13M | 16±20% | 3 | 0.338 | 560 |  |  |  |  |  |  |  |  |
| 126 | WMF21-18D-13M | 18±20% | 3 | 0.356 | 560 |  |  |  |  |  |  |  |  |
| 127 | WMF21-20D-13M | 20±20% | 3 | 0.372 | 560 |  |  |  |  |  |  |  |  |
| 128 | WMF21-30D-13M | 30±20% | 2.5 | 0.517 | 560 |  |  |  |  |  |  |  |  |
| 129 | WMF21-47D-13M | 47±20% | 2 | 0.810 | 470 |  |  |  |  |  |  |  |  |
| 130 | WMF21-60D-13M | 60±20% | 2 | 1.217 | 470 |  |  |  |  |  |  |  |  |
| 131 | WMF21-120D-13M | 120±20% | 1.5 | 2.124 | 470 |  |  |  |  |  |  |  |  |
| 132 | WMF21-0.7D-15M | 0.7±20% | 8 | 0.038 | 680 | Approx. 21 | Approx. 75 | 3.5 | -40~+200 | 16.5 | 6 | 0.8/1.0 | 7.5 (10) |
| 133 | WMF21-1D-15M | 1±20% | 8 | 0.044 | 680 |  |  |  |  |  |  |  |  |
| 134 | WMF21-1.3D-15M | 1.3±20% | 8 | 0.048 | 680 |  |  |  |  |  |  |  |  |
| 135 | WMF21-1.5D-15M | 1.5±20% | 8 | 0.052 | 680 |  |  |  |  |  |  |  |  |
| 136 | WMF21-2D-15M | 2±20% | 7 | 0.057 | 680 |  |  |  |  |  |  |  |  |
| 137 | WMF21-2.2D-15M | 2.2±20% | 7 | 0.059 | 680 |  |  |  |  |  |  |  |  |
| 138 | WMF21-2.5D-15M | 2.5±20% | 7 | 0.062 | 610 |  |  |  |  |  |  |  |  |
| 139 | WMF21-3D-15M | 3±20% | 7 | 0.075 | 610 |  |  |  |  |  |  |  |  |
| 140 | WMF21-4D-15M | 4±20% | 6 | 0.084 | 610 |  |  |  |  |  |  |  |  |
| 141 | WMF21-4.7D-15M | 4.7±20% | 6 | 0.097 | 610 |  |  |  |  |  |  |  |  |
| 142 | WMF21-5D-15M | 5±20% | 6 | 0.112 | 610 |  |  |  |  |  |  |  |  |
| 143 | WMF21-6D-15M | 6±20% | 5 | 0.155 | 610 |  |  |  |  |  |  |  |  |
| 144 | WMF21-7D-15M | 7±20% | 5 | 0.173 | 610 |  |  |  |  |  |  |  |  |
| 145 | WMF21-8D-15M | 8±20% | 5 | 0.178 | 610 |  |  |  |  |  |  |  |  |
| 146 | WMF21-10D-15M | 10±20% | 5 | 0.180 | 610 |  |  |  |  |  |  |  |  |
| 147 | WMF21-12D-15M | 12±20% | 4 | 0.250 | 610 |  |  |  |  |  |  |  |  |
| 148 | WMF21-15D-15M | 15±20% | 4 | 0.268 | 610 |  |  |  |  |  |  |  |  |
| 149 | WMF21-16D-15M | 16±20% | 4 | 0.276 | 610 |  |  |  |  |  |  |  |  |
| 150 | WMF21-18D-15M | 18±20% | 4 | 0.282 | 560 |  |  |  |  |  |  |  |  |
| 151 | WMF21-20D-15M | 20±20% | 4 | 0.288 | 560 |  |  |  |  |  |  |  |  |
| 152 | WMF21-25D-15M | 25±20% | 3.5 | 0.396 | 560 |  |  |  |  |  |  |  |  |
| 153 | WMF21-30D-15M | 30±20% | 3.5 | 0.438 | 470 |  |  |  |  |  |  |  |  |
| 154 | WMF21-33D-15M | 33±20% | 3 | 0.485 | 470 |  |  |  |  |  |  |  |  |
| 155 | WMF21-40D-15M | 40±20% | 3 | 0.572 | 470 |  |  |  |  |  |  |  |  |
| 156 | WMF21-47D-15M | 47±20% | 3 | 0.680 | 470 |  |  |  |  |  |  |  |  |
| 157 | WMF21-50D-15M | 50±20% | 2.5 | 0.725 | 470 |  |  |  |  |  |  |  |  |
| 158 | WMF21-120D-15M | 120±20% | 2 | 1.652 | 470 |  |  |  |  |  |  |  |  |
| 159 | WMF21-0.7D-20M | 0.7±20% | 12 | 0.018 | 1000 | Approx. 28 | Approx. 113 | 5.0 | -40~+200 | 21.5 | 7 | 1.0 | 7.5 (10) |
| 160 | WMF21-1D-20M | 1±20% | 10 | 0.028 | 1000 |  |  |  |  |  |  |  |  |
| 161 | WMF21-1.3D-20M | 1.3±20% | 9 | 0.037 | 1000 |  |  |  |  |  |  |  |  |
| 162 | WMF21-1.5D-20M | 1.5±20% | 9 | 0.039 | 1000 |  |  |  |  |  |  |  |  |
| 163 | WMF21-2D-20M | 2±20% | 8 | 0.044 | 1000 |  |  |  |  |  |  |  |  |
| 164 | WMF21-2.2D-20M | 2.2±20% | 8 | 0.048 | 1000 |  |  |  |  |  |  |  |  |
| 165 | WMF21-2.5D-20M | 2.5±20% | 8 | 0.051 | 1000 |  |  |  |  |  |  |  |  |
| 166 | WMF21-3D-20M | 3±20% | 8 | 0.055 | 1000 |  |  |  |  |  |  |  |  |
| 167 | WMF21-3.3D-20M | 3.3±20% | 8 | 0.061 | 1000 |  |  |  |  |  |  |  |  |
| 168 | WMF21-4D-20M | 4±20% | 7 | 0.071 | 1000 |  |  |  |  |  |  |  |  |
| 169 | WMF21-4.7D-20M | 4.7±20% | 7 | 0.082 | 1000 |  |  |  |  |  |  |  |  |
| 170 | WMF21-5D-20M | 5±20% | 7 | 0.087 | 1000 |  |  |  |  |  |  |  |  |
| 171 | WMF21-6D-20M | 6±20% | 6 | 0.113 | 1000 |  |  |  |  |  |  |  |  |
| 172 | WMF21-6R8D-20M | 6.8±20% | 6 | 0.130 | 1000 |  |  |  |  |  |  |  |  |
| 173 | WMF21-7D-20M | 7±20% | 6 | 0.133 | 1000 |  |  |  |  |  |  |  |  |
| 174 | WMF21-8D-20M | 8±20% | 6 | 0.142 | 1000 |  |  |  |  |  |  |  |  |
| 175 | WMF21-10D-20M | 10±20% | 6 | 0.162 | 1000 |  |  |  |  |  |  |  |  |
| 176 | WMF21-12D-20M | 12±20% | 5 | 0.195 | 1000 |  |  |  |  |  |  |  |  |
| 177 | WMF21-15D-20M | 15±20% | 4.5 | 0.233 | 1000 |  |  |  |  |  |  |  |  |

| No. 序号 | Part No. 产品编号 | Rated Zero-power Resistance 额定 零功率电阻 RN (Ω) | Max. Steady State Current 最大 稳态电流 Imax (A) | Remain. Resistance 残余电阻 RR (Ω) | Max.Load Capacitancein in uF 最大允许 容量 @ 240VAC (uF) | Thermal Dissipation Constant 热耗散 系数 δ(mW/℃) | Thermal Time Constant 热时间 常数 τ(Sec) | Max.power Rating 最大额定 功率 @ 25℃ Pmax(W) | Operating Temperature工作温度 (℃) | Dimensions 外形尺寸 (mm) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | DMax | TMax | d±0.05 | F±1 |
| 178 | WMF21-16D-20M | 16±20% | 4.5 | 0.242 | 1000 | Approx. 28 | Approx. 113 | 5.0 | -40~+200 | 21.5 | 7 | 1.0 | 7.5 (10) |
| 179 | WMF21-18D-20M | 18±20% | 4 | 0.282 |  |  |  |  |  |  |  |  |  |
| 180 | WMF21-20D-20M | 20±20% | 4 | 0.306 |  |  |  |  |  |  |  |  |  |
| 181 | WMF21-25D-20M | 25±20% | 4 | 0.341 | 820 |  |  |  |  |  |  |  |  |
| 182 | WMF21-30D-20M | 30±20% | 4 | 0.365 |  |  |  |  |  |  |  |  |  |
| 183 | WMF21-47D-20M | 47±20% | 3.5 | 0.422 |  |  |  |  |  |  |  |  |  |
| 184 | WMF21-0.7D-22M | 0.7±20% | 12 | 0.027 | 1100 | Approx. 28 | Approx. 120 | 6.0 | -40~+200 | 24.5 | 7.5 | 1.0 | 7.5 (10) |
| 185 | WMF21-1D-22M | 1±20% | 10 | 0.037 |  |  |  |  |  |  |  |  |  |
| 186 | WMF21-1.3D-22M | 1.3±20% | 9 | 0.045 |  |  |  |  |  |  |  |  |  |
| 187 | WMF21-1.5D-22M | 1.5±20% | 9 | 0.053 |  |  |  |  |  |  |  |  |  |
| 188 | WMF21-2D-22M | 2±20% | 8 | 0.066 |  |  |  |  |  |  |  |  |  |
| 189 | WMF21-2.2D-22M | 2.2±20% | 8 | 0.069 |  |  |  |  |  |  |  |  |  |
| 190 | WMF21-2.5D-22M | 2.5±20% | 8 | 0.072 |  |  |  |  |  |  |  |  |  |
| 191 | WMF21-3D-22M | 3±20% | 8 | 0.087 |  |  |  |  |  |  |  |  |  |
| 192 | WMF21-4D-22M | 4±20% | 7 | 0.092 |  |  |  |  |  |  |  |  |  |
| 193 | WMF21-5D-22M | 5±20% | 7 | 0.098 |  |  |  |  |  |  |  |  |  |
| 194 | WMF21-6D-22M | 6±20% | 6 | 0.125 |  |  |  |  |  |  |  |  |  |
| 195 | WMF21-8D-22M | 8±20% | 6 | 0.145 |  |  |  |  |  |  |  |  |  |
| 196 | WMF21-10D-22M | 10±20% | 6 | 0.173 |  |  |  |  |  |  |  |  |  |
| 197 | WMF21-12D-22M | 12±20% | 5 | 0.216 |  |  |  |  |  |  |  |  |  |
| 198 | WMF21-15D-22M | 15±20% | 4.5 | 0.254 |  |  |  |  |  |  |  |  |  |
| 199 | WMF21-16D-22M | 16±20% | 4.5 | 0.282 |  |  |  |  |  |  |  |  |  |
| 200 | WMF21-20D-22M | 20±20% | 4 | 0.362 |  |  |  |  |  |  |  |  |  |
| 201 | WMF21-0.7D-25M | 0.7±20% | 13 | 0.014 | 1200 | Approx. 30 | Approx. 130 | 7.0 | -40~+200 | 26.5 | 8 | 1.0 | 10 |
| 202 | WMF21-1D-25M | 1±20% | 12 | 0.019 |  |  |  |  |  |  |  |  |  |
| 203 | WMF21-1.3D-25M | 1.3±20% | 11 | 0.024 |  |  |  |  |  |  |  |  |  |
| 204 | WMF21-1.5D-25M | 1.5±20% | 10 | 0.027 |  |  |  |  |  |  |  |  |  |
| 205 | WMF21-2D-25M | 2±20% | 9 | 0.033 |  |  |  |  |  |  |  |  |  |
| 206 | WMF21-3D-25M | 3±20% | 9 | 0.044 |  |  |  |  |  |  |  |  |  |
| 207 | WMF21-5D-25M | 5±20% | 8 | 0.070 |  |  |  |  |  |  |  |  |  |
| 208 | WMF21-6D-25M | 6±20% | 7 | 0.082 |  |  |  |  |  |  |  |  |  |
| 209 | WMF21-8D-25M | 8±20% | 7 | 0.114 |  |  |  |  |  |  |  |  |  |
| 210 | WMF21-10D-25M | 10±20% | 7 | 0.130 |  |  |  |  |  |  |  |  |  |
| 211 | WMF21-12D-25M | 12±20% | 6 | 0.156 |  |  |  |  |  |  |  |  |  |
| 212 | WMF21-15D-25M | 15±20% | 6 | 0.159 |  |  |  |  |  |  |  |  |  |
| 213 | WMF21-16D-25M | 16±20% | 6 | 0.160 |  |  |  |  |  |  |  |  |  |
| 214 | WMF21-20D-25M | 20±20% | 5 | 0.182 |  |  |  |  |  |  |  |  |  |